SPECIFICATION

FOR

ELECTRICAL HEAT

TRACING CABLES

June 2005

ELECTRIC HEAT TRACING CABLES SPECIFICATION

TABLE OF CONTENTS

PAGE

1.0	HEATER CABLES	3

1.1  SELF-REGULATING	3

1.2  FLEXIBLE SERIES RESISTANCE	5

1.3  MINERAL INSULATED (M.I)	5

1.4  METALLIC BRAIDS AND OVERJACKETS	6

2.0	SKIN EFFECT HEAT TRACING	7

1.0	HEATER CABLE

The following heater cables are approved for use on this project.  The heat tracing contractor shall be responsible for selecting the type of heating cable to be used for a given application.

1.1	Self-Regulating Heating Cable

A.	Low Temperature - Self-Regulating Heating Cable

1.	Heating cables shall be self-regulating, capable of maintaining process temperatures up to 65°C and a continuous exposure to pipeline temperature of 85°C while de-energized.

2.	Cable must be of parallel construction so that it can be cut to length without changing its power output per unit length.

3.	The heater cable assembly shall consist of two parallel 1.3 mm2 nickel-plated copper bus wires with a semiconductive PTC polymer extruded over and between these parallel conductors, forming a continuous matrix heating element.  There shall be an insulating jacket of polyethylene is then extruded over the heating element core.

4.	The semiconductive heating matrix and primary insulating jacket shall be cross-linked by irradiation.

5.	The basic cable will be covered by means of a metallic braid of nickel plated or tinned copper.  The braid will provide a nominal coverage of eighty percent (80%) and will exhibit a resistance not exceeding 0.010 ohm/m.

6.	For applications with exposure to corrosive solutions, cable shall be further covered with a polyolefin overjacket (for applications with exposure to aqueous organic solutions).

7.	For applications with exposure to corrosive solutions, cable shall be further covered with a fluoropolymer overjacket (for exposure to hydrocarbon based inorganic solutions).

8.	For longer circuit lengths and higher heat loss requirements greater than 33 W/m @10°C, 2.1 mm2 nickel-plated copper bus wires will be used.

- Long term stability shall be established by the service life performance test per IEEE 515 Std-2004.

# B.	Medium Temperature Self-Regulating Heating Cables

1.	Heating cables shall be self-regulating, capable of maintaining temperatures up to 121°C and withstanding an intermittent pipeline exposure temperature of 215°C while energized and 250°C de-energized. Additionally, the cable shall have a continuous exposure temperature rating of 205°C while de-energized.

2.	Cable must be parallel construction so that it can be cut to length without changing its power output per unit length.

- The heater cable assembly shall consist of two parallel 1.3 mm2 nickel-plated copper bus wires with a semiconductive PTC polymer extruded over and between these parallel conductors, forming a continuous matrix heating element.  There shall be a fluoropolymer insulating jacket is then extruded over the heating element core.

- The basic cable will be covered by means of a metallic braid of nickel-plated copper or tinned copper.  The braid will provide a nominal coverage of eighty percent (80%) and will exhibit a resistance not exceeding 0.010 ohm/m.

5.	The cable shall be covered with a fluoropolymer overjacket.

6. 	Long term stability shall be established by the service life performance test per IEEE 515 Std-2004.

# C.	High Temperature Self-Regulating Heating Cables

- Heating cables shall be self-regulating, capable of maintaining temperatures up to 149°C and withstanding an intermittent pipeline exposure temperature of 230°C while energized. Additionally, the cable shall have a continuous exposure temperature rating of 205°C while de-energized.

- Cable must be parallel construction so that it can be cut to length without changing its power output per unit length.

- The heater cable assembly shall consist of two parallel 2.1 mm2 nickel-plated copper wires.  A semiconductive PTC polymer is extruded over and between these parallel conductors, forming a continuous matrix heating element.  A high temperature fluoropolymer insulating jacket is then extruded over the heating element core.

- The basic cable will be covered by means of a metallic braid of nickel-plated copper.  The braid will provide a nominal coverage of eighty percent (80%) and will exhibit a resistance not exceeding 0.010 ohm/m.

- The cable shall be covered with a high temperature fluoropolymer overjacket.

- Long term stability shall be established by the service life performance test per IEEE 515 Std-2004.

D.	High Temperature Power Limiting Heating Cables

- Power Limiting heating cables shall be used to maintain temperatures to 149°C and a continuous exposure to pipeline temperature of 260°C when the cable is de-energized.

- Power limiting heating cables shall consist of two 3.3  mm2 nickel-plated copper bus wires, individually insulated with a high temperature fluoropolymer. One of the bus conductors will be alternately exposed for connection to the heating element at regular intervals.

- A PTC (Positive Temperature Coefficient) conductor shall be spirally wrapped around a fiberglass carrier strand to form a coiled resistor heating element.  This coiled resistor element shall be helically wrapped around the insulated voltage supply bus wires making electrical contact with alternate bus wires at regular intervals to complete the heating circuit.

- There shall be a fiberglass composite between the heating element and primary dielectric jacket.

- The basic cable will be covered by means of a metallic braid of nickel-plated copper.  The braid will provide a nominal coverage of eighty percent (80%) and will exhibit a resistance not exceeding 0.010 ohm/m.

- For applications subject to corrosive atmospheres, cable shall be covered with a high temperature fluoropolymer overjacket.

- Long term stability shall be established by the service life performance test per IEEE 515 Std-2004.

1.2	Flexible Series Resistance Heat Tracing

- Flexible Series Resistance Heating Cables shall be in two or three conductor configurations.  Conductor type shall be nickel-plated copper and available in various sizes, ranging from 1.3 mm2 to  5.3 mm2  to ensure required circuit resistance can be designed.

B.	Electrical insulation shall be fluoropolymer rated for 600 Vac, with a capability of withstanding continuous exposure to temperatures up to 204 °C/260 °C when the circuit is de-energized.  For temperature exposures greater than 204 °C the cable shall have a fiberglass composite between the conductor and jacket.  The insulated conductors shall then be connected to approved cold lead and end termination assemblies.

  - Mineral Insulated (M.I.) Heating Cable

A.	M.I. cables shall be capable of continuous exposure to temperatures of 593 °C when the cable is de-energized.

B.	M.I. heating cable shall be one or two heating conductors with magnesium oxide insulation and an INCOLOY 825 sheath.  Cable voltage rating shall be either 300 Vac or 600 Vac. The complete heater assembly shall be approved for use in the area it will be installed.

C.	Each M.I. heater shall be factory fabricated to required lengths with cold junctions for connection to power or where splices are required.  Cold sections shall be 1.2 m or 2.1 m long with 20 cm long thermoplastic insulated leads.  Cold sections shall have a gland type fitting for termination in threaded hub junction boxes.  Cables shall be factory terminated and sealed.

D.	The M.I. cable sheath shall be seamless.  Welded sheaths shall be provided only with owner's engineer approval.

- Each M.I. cable shall have a stainless steel tag connected to the cold sections.  The tag shall show the circuit number to which it is   connected, and heater electrical and physical characteristics such as voltage, current, watts/ft, cold lead length, and resistance @ 20 ºC.

1.4	All heating cables, except M.I. type, shall have a metallic braid for use as a ground path.  An overjacket shall also be required for all heating cables. For low temperature heating cables the overjacket material shall meet the requirements in the application as defined below:

A.	For low temperature heating cables polyolefin overjacket shall be used in moderately corrosive areas and where exposure to aqueous inorganic compounds are expected.

B.	For medium to high temperature heating cables a fluoropolymer overjacket shall be used over the metallic braid in severely corrosive areas where exposure to hydrocarbon based chemical solutions or vapors is expected.

2.0	SKIN-EFFECT HEAT TRACING

A. 	Low/Medium Temperature - Skin Effect Heat Tracing

1.  	Skin effect conductors shall be insulated with special grade HDPE insulation.  The conductors shall be stranded, Class H, nickel-plated copper or tinned copper.  The conductors shall be insulated with polyolefin with a temperature rating of 125 °C with minimal airspace between the conductor strands and extruded dielectric.  There shall be outer scuff HDPE jacket extruded over the primary polyolefin jacket.

- The skin effect conductors shall meet the type test requirements in the IEEE 844 Std-2000.

B.	High Temperature - Skin Effect Heat Tracing

1.	Skin effect conductors shall be stranded, Class H, nickel-plated copper.  The conductors shall be insulated with a high temperature fluoropolymer dielectric with a minimum temperature rating of 204° C with minimal airspace between the conductor strands and extruded dielectric.  There shall be an outer scuff flouropolymer jacket extruded over the primary fluoropolymer jacket.

2.	The skin effect conductors shall meet the type test requirements in the IEEE 844 Std-2000.